## Sheet1
APPROVED PRODUCTS LIST - WASTEWATER (Updated May 2025)
Product | Type | Specifications | Manufacturer | Description/Model | Comments
Main Line Non-Pressure Pipe | Polyvinyl Chloride (PVC) Solid Wall 200mmø to 400 mmø inclusive | CSA B182.2 DR 35 minimum ASTM D3034 Minimum pipe stiffness - 320 kPa | Ipex Inc. | Ring Tite
Enviro Tite
|  |  | Groupe Brunet | Duraloc | Rubber gasket bell and spigot joints
|  |  | National Pipe & Plastics Inc. | Ever-Green | Green in colour
JM Eagle
|  |  | West Lake Pipe | Royal Seal
|  |  | Diamond Plastic Corp. | SANI-21
| Polyvinyl Chloride (PVC) Solid Wall 450mmø to 525mmø | CSA B182.2 DR 35 minimum ASTM D3034 Minimum pipe stiffness - 320 kPa | Ipex Inc. | Ring Tite
|  |  | Groupe Brunet | Duraloc
|  |  | National Pipe & Plastics Inc. | Ever-Green | Rubber gasket bell and spigot joints
|  |  | Diamond Plastic Corp. Sani 21 | SANI-21 | Green in colour
|  |  | West Lake Pipe | Royal Seal
| Concrete with HDPE Liner up to 675mm | CSA 257.2 ASTM C76 & ASTM C361 | Con Cast Pipe | 600mm, 900mm, 1200mm | Manufactured at a prequalified plant and marked with a "Prequalification Stamp" (triangular symbol)
| Concrete up to and including 900mm ø | CSA A257.1, A 257.2 and A257.3 (whichever applies) OPSS 1820 |  |  | Manufactured at a prequalified plant and marked with a "Prequalification Stamp" (triangular symbol)
| Concrete larger than 900mm ø | CSA A257.2 Joints - CSA A257.3 OPSS 1820 |  |  | Manufactured at a prequalified plant and marked with a "Prequalification Stamp" (triangular symbol)
| High Density Polyethylene (HDPE) | ASTM F894 Minimum pipe stiffness - 320 kPa CSA B182.6 | Infra Pipe Solutions | Weholite | Smooth outer and smooth inner walls
|  |  | Armtec | BOSS Poly-Tite | All pipe to have a light coloured interior to facilitate CCTV Inspections Pipe to be installed through MH's in a continuous fashion, as per manufacturers recommendations
Service Connections | Vitrified Clay | CSA A60.1M Joints - CSA A60.3M
| Polyvinyl Chloride (PVC) Solid Wall | CSA B182.1 ASTM D 3034 STD DWGS 2-4 Fittings - ASTM D 3034 Minimum pipe stiffness - 630 kPa (SDR 28) | Ipex |  | Rubber gasket bell and spigot joints White only for storm water connections
West Lake Pipe
Diamond
National
Groupe Brunet
Saddles | Concrete and Vitrified Clay Pipe | Factory Made Tees are to be used for any new construction STD DWGS 2-4-1, 2-4-2 | NPC Inc. | Kor-N-Tee | Concrete pipe only 300mm ø and larger
|  |  | Romac Industries | CB - Sewer Saddle
|  |  | Galaxy Plastics | Core-Bell Adapter | Concrete pipe only
|  |  | Crowle | Cast Iron Sadldes
| PVC Pipe | Factory Made Tees are to be used for any new construction STD DWGS 2-4-1, 2-4-2 | Crowle | Cast Iron Sadldes | CSA B182.2 (ASTM D3034) Pipe only
|  |  | Romac Industries | CB - Sewer Saddle
|  |  | NPC Inc. | Kor-N-Tee Saddle
Ipex
|  |  | West Lake Pipe | "Epoxy On" Saddle | CSA 182.4 (ASTM D3034) Pipe only
Couplings |  |  | Rollee | Kwik Coupling
|  |  | Mission Rubber Co. | Adjustable Repair Couplings (ARC)
|  |  | Fernco Couplings | RC Series
5000 Series
|  |  | Straub Tadco Manufacturing | Straub Flex/Open
Straub Grip
|  |  | Preper-PLS | Preper
Joint Restraints | PVC Pipe |  | Ford Meter Box Co. Inc. | UniFlange Series 1300C | PVC pipe used with Mech Joint/Push-On Fittings
|  |  |  | UniFlange Series 1350C | For PVC pipe bell Joints
|  |  |  | UniFlange Series 1500C | MJ retainer gland joint restraint
| Ductile Iron Pipe |  | Ford Meter Box Co. Inc. | UniFlange Series 1390D, 1400D
Test Fittings | Cast Iron |  | Crowle |  | Marked "SAN" in accordance to STD DWG 2-4-3
| PVC | 100 x 125; 100 x 100 & 100x100x125 wye | Ipex
Repair Clamps |  | CSA B 602 | Rollee | Kwik Coupling
|  |  | Mission Rubber Co. | Flex-Seal - ARC
|  |  | Cambridge Brass | Series 425
|  |  | Romac Industries | SS Repair Clamp
Service Plugs | Plastic | SDR 35 CSA B182.2 | Galaxy Plastics | Tigre
Zinc Plated
| Epoxy Coated |  | Crowle
Pressure Pipe (Forcemains) | Polyvinyl Chloride (PVC) 100mm to 525mm | CSA B 137.3 Joints - ASTM D3139 | Ipex
|  |  | National | DR 26
|  |  | Diamond |  | Green in Colour
|  |  | West Lake Pipe | IPS Series DR26, 40 to 300mm | Installed with 12 Gauge stranded tracer wire
|  |  |  | Green C900, DR18 | Bell and spigot joints
|  |  | Next Polymers Groupe Brunet | Duraloc, DR 26
| High Density Polyethylene (HDPE) 100mm to 525mm | CSA B137.0, B137.1 ASTM D3035, D3350 or CG 5 Spec. 41-GP-25M DR 28 minimum (size and class as per design) | Infra Pipe Solutions | Sclairpipe | Jointed by thermal butt fusion or flange
|  |  | Oxford Plastics | PE3408/3608 | Installed with 12 Gauge stranded tracer wire, 4 x 12 Gauge stranded tracer wire for HDD installations
| Concrete Pressure Pipe 600mm and above | AWWA C300, C301 or C303 | Rinker Materials |  | Bell and spigot joints Installed with tracer wire Joints sealed with cement grout and foam diapers Shop drawings shall be supplied to the Region for review and approval prior to construction
Decast
Fittings | Cast Iron and Ductile Iron | ANSI A21.10 AWWA C111 Furnished with mechanical or push-on Tyton joinys - ANSI A21.11, AWWA C111 Flanged End rated at 125 psi for PE pipe installations | Sigma
Star
Bibby
| Ductile Iron Compact Fittings Long Body | ANSI C110/A21.10, C111/A21.11, C104/A21.4 | SIP Industries |  | Mechanical joint & flanged joint full body (Long Body) ductile iron fittings for the connection and or redirection of underground or above ground ductiole, PVC< PVOCO< HDPE pipping & flanged piping
| Polyvinyl Chloride (PVC) up to 525 mm | Used with PVC pipe only CSA B137.0, B137.1 CSA B182.2 ASTM D3034 - Solid Wall | Ipex
Pro-Line
West Lake Pipe
|  |  | Galaxy Plastics | Fabricated
GPK
Air Release Valves | Combination Air Release / Vacuum Breaker |  | Crispin Valve | S/LS Series
|  |  | Vent-O-Mat | Sewer RGX Series
|  |  | Val-Matic |  | Shall be tall bodied valves complete with flushing port and
|  |  | A.R.I. | D020 | flood safe (refer to Std drwg 1-3-12)
D025P
D025SS
Check Valves | Duckbill | C.S.A Z299.3-85 | EVR | CPO, CPI CPJ, CPF | Approved for use in Wastewater Applications only
| Duckbill (Red Valve) |  | Tideflex | TF-1, TF-2, Series 35,35-1, 37
| Swing Flex |  | Val-Matic | Series 500
| Rubber Flapper/Swing Flex Check Valves |  | DeZURIK/Apco | Series 100
Casing Spacers |  |  | Cascade | CCS08 and CCS12 | Ultra high molecular weight polymer runners (or equivalent)
|  | T-304 Stainless Steel | CCI Pipeline Systems | CSS8 and CSS12 | Position of pipe within liner to be centered and restrained, sufficient to provide no less than 19mm clearance between casing and bell of pipe
|  |  | Utility Supply Corp | SSI | Pipe restrained laterally for the entire length of the liner
|  |  | BWM |  | Sealed using wrap around rubber ends complete with stainless steel (T-304) banding
Precast Maintenance Hole | Concrete | CSA A257.4 ASTM C-478 OPSS 1351 STD DWGS 2-5-1 to 2-5-12 | Con Cast Pipe
|  |  | Omni Precast |  | Includes precast drop structure
|  |  | Rinker Materials |  | Factory cast rubber boot (flexible, water tight) required at pipe connections
Decast
| Pre-Benched | Same as Concrete | Con Cast Pipe |  | For 200mm and 250mm inlet and outlet pipes only
Maintenance Hole Frame & Cover | Standard | STD DWGS 2-5-13, 2-5-14, 2-5-25 & 2-6 OPSD 401.01 | Bibby Ste. Croix
Delta
EJ
Cedar Infrastructure Products
Sigma Corp.
| Water Tight Circular Frame & Cover | ASTM A46 CL35B | Hamilton Kent | Lifespan | Not for use in road allowance. Follow Manufacturer's instructions if using with Cretex Pro Ring
| Water Tight Square Frame & Cover | STD DWG 2-6-4 OPSD 401.03, no lugs | EJ
Star Pipe Products
Cedar Infrastucture Products
Bibby Ste. Croix
Maintenance Hole Circular Frame and Cover |  | STD DWGS 2-6-1, 2-6-2 OPSD 401.02 | EJ | Selflevel Assembly
1040/1040A
Cedar Infrastucture Products
Bibby Ste. Croix
Maintenance Hole Adjusment Units | Pre-Cast Concrete |  | Decast
|  |  | Rinker Materials | Moduloc
| HD Rubber | OPSS 1853/ASTM D 412 | Hamilton Kent | Lifespan
| Polyethylene |  | Ipex | Lifesaver
Protective Coatings | Corrosion Prevention Tape | ANSI / AWWA C-217 | Denso North America Inc. | Corrosion Protection System | Denso Paste, LT Tape and Profiling Mastic
|  |  | Advanced Corrosion Sys | Petro guard System | Paste PP04ST, Mastic PM3ST, Tape PTLT
|  |  | Petro Coating Systems | PCS System | PT150ST, PP04 and PM3ST (Primer, Paste and Tape)
|  |  | RPH Distributors |  | TC Envirotape, Enviroprime and Enviromastic
| MIC Protection | STD DWG 2-5-1 | W.R. Meadows | Cem-Kote Flex CR
Cretex Easyseal
Maintenance Hole Waterproofing | Sealant | STD DWG 2-5-1 | Hydrotite | Leakmaster
CN2000
| Membrane | ASTM D 412 STD DWG 2-5-25 | W.R. Meadows | Mel-Rol | Use with Mel-Rol Strips
| Grout | STD DWG 2-8-1 | Multiurethanes | Multi-Gel | Hydrophilic Injection
Maintenance Hole Venting | Vent Pipe | STD DWGS 2-5-2, 2-5-22 |  | 304 SS
| Pipe Insect screen | STD DWGS 2-5-2, 2-5-22 | Wager | 1700 | Float style check valve vent outlet
|  |  | Wager | 1850 | Check valve with odor cannister
Maintenance Hole Hardware | Steps | STD DWG 2-6-11 |  | Aluminum
| Anchors | 316 SS | Hilti | Kwik Bolt
For PCCP Systems, See Sanitary Sewer Dwgs Series 2-7