## Sheet1
APPROVED PRODUCTS LIST - WATER (Updated May 2025)
*All listed water appurtenances must comply to NSF 61 standards
Product | Type | Specifications | Manufacturer | Description/Model | Comments
Pipe Up To and Including 400mm Diameter | Ductile Iron | Class 52 ANSI A21.51 (AWWA C151) Cement-mortor lined as per ANSI A21.4 (AWWA C104) Installed with polyethylene encasment as per ANSI A21.5 (AWWA C105) | Canada Pipe | Class 52 | Furnished with push-on Tyton® Joints as per ANSI A21.11 (AWWA C111) Polyethylene encasement shall be installed in accordance with manufacturers specifications and instructions
| Polyvinyl Chloride (PVC ) | DR 18 AWWA C900 | Ipex | Blue Brute
|  |  | National Pipe | Dura Blue | Rubber gasketed bell and spigot joints
|  |  | Groupe Brunet | Aqualoc | Installed with 12 Gauge stranded tracer wire
|  |  | Diamond Plastics Corp. | PR 235 | Joints restrained where required by design and wrapped with corrosion protective system
|  |  | West Lake Pipe | Aquaspring C900
| Molecularly Oriented Poly Vinyl Chloride PVCo | Pressure Rating 235 psi AWWA 909 CSA B137.3 | Ipex | Bionax | Rubber gasketed bell and spigot joints Installed with 12 Gauge stranded tracer wire
|  |  | West Lake Pipe | Aquamax C909 | Joints restrained where required by design and wrapped with corrosion protective system
| Concrete Pressure Pipe Up to 400mm | AWWA C300, C301 and C302 | Rinker Materials |  | Supplied with Bell and spigot joints Joints sealed with cement grout and foam diapers
|  |  | Decast |  | Shop drawings shall be supplied to Peel for review and approval prior to construction Restrained where required by design
Fittings | Cast Iron and Ductile Iron Long Body | ANSI A21.10 AWWA C110 Cement-mortor lined as per ANSI A21.4 (AWWA C104) | Sigma |  | Furnished with push-on Tyton Joints as per ANSI A21.11 (AWWA C111) complete with T-304 stainless steel nuts and bolts
Star Pipe Products
| Ductile Iron Compact Fittings Short Body | ANSI A21.53 AWWA C153/C111 Cement-mortor lined as per ANSI A21.4 (AWWA C104) | Sigma |  | Mechanical type ends Polyethylene encasement shall be installed in accordance with manufacturers specifications and instructions or wrapped with corrosion protection system
SIP Industries
Star Pipe Products
| Ductile Iron Compact Fittings Long Body | ANSI C110/A21.10, C111/A21.11, C104/A21.4 | SIP Industries |  | Mechanical joint & flanged joint full body (Long Body) ductile iron fittings for the connection and or redirection of underground or above ground ductiole, PVC< PVOCO< HDPE pipping & flanged piping
| Polyvinyl Chloride (PVC) up to 200mm Diameter | AWWA C907 CSA B137.2 | Ipex |  | PVC Fittings to have fitting pipe restrainers Joints restrained where required by design and wrapped with corrosion protection system Complete with T-304 stainless steel nuts and bolts
| Polyvinyl Chloride (PVC) 250mm & 300mm Diameter | AWWA C900 CSA B137.3 | Ipex |  | PVC Fittings to have fitting pipe restrainers Joints restrained where required by design and wrapped with corrosion protection system Complete with T-304 stainless steel nuts and bolts
West Lake Pipe
Galaxy Plastics
| Victaulic |  |  |  | Acceptable for all AWWA approved pipes excluding PVC
Protective Coatings | Corrosion Prevention System (3 stage system) Applied to all metallic fittings and components | AWWA C-217 | Denso North America Inc. | Denso System | Denso Paste, LT Paste, Profiling Mastic
|  |  | Petro Coating Systems | PCS System
|  |  | Interprovincial Corrosion Control LTD | Petro Wrap System | Petroleum Wax Tape, Primer, Mastic
|  |  | RPH Distributors |  | TC Envirotape, Enviroprime and Enviromastic
|  |  | Advanced Corrosion Sys | Petro guard System | Paste PP04ST, Mastic PM3ST, Tape PTLT
|  |  | River Run Industrial | Longwrap Perolatum Tape System | Petrolatum paste, Mastic and Tape
|  |  | Seal for Life Industries | Stopaq | Stopaq Paste, Putty, Wrapping band
Joint Restraints | For PVC Pipe | ASTM F1674 All complete with 304 stainless steel nuts & bolts | Star Pipe Products Inc | PVC Ring Lock PVC grip | Installed with concrete thrust blocks (on existing pipe only)
|  |  |  | PVC Stargrip 4000 G2 | in accordance with OPS standards
Stargrip 4300 Series
|  |  |  | 1000-C | MJ fittings only
|  |  | Clow Canada | Tufgrip Dual Wedge | Orange colour coded 1500 series
|  |  |  | Series 90 | Flange Adapter
|  |  |  | Series 300, 350, 360 | Restrainers
|  |  | SIP Industries Inc | EZ Grip PTP Series | Bell joint restraint
|  |  |  | EZ Grip for PVC | Red colour coded
|  |  | Smith-Blair | 111 & 120 | Cam lock
|  |  | Sigma Corp | PV-Lok series PWM, PWP and PWPF
One-Lok SLC
|  |  | Georg Fisher | Multijoint 3000 Plus | Transitional Joint Restraint System for HDPE
|  |  | EBAA Iron Sales Inc. | Megalug Series | 1500, 1600, 2000, 2600
|  |  | Romac Industries Inc. | Grip Ring
|  |  | Ford Meter Box Co. Inc. | UniFlange Series 1300C | PVC pipe used with Mech Joint/Push-On Fittings
|  |  |  | UniFlange Series 1350C | For PVC pipe bell Joints
|  |  |  | UniFlange Series 1500C | MJ retainer gland joint restraint
| For PVCO Pipe to PVC Fittings | ASTM F1674 100mm to 300mm | Ford Meter Box Co. Inc. | Uni-Flange UFR 1369
|  |  | EBAA Iron Sales Inc. | 2600
|  |  | Sigma | PV-Lok PWPF
|  |  | Star Pipe Products Inc | 1000-1100-1200G2
|  |  |  | Stargrip 4300 Series | Orange colour coded
|  |  | Clow Canada | Tufgrip Dual Wedge | Orange colour coded 1500 series
360c
390c
|  |  | SIP Industries Inc | EZ Grip Model PTPFC
|  | 400mm | Sigma | PV-Lok PWPF
|  |  | Star Pipe Products Inc | 1200R Series
Joint Restraints | For PVCO Pipe Bell and Spigot Push-On Joints | ASTM F1674 100mm to 300mm | Clow Canada | Tufgrip Dual Wedge | Orange colour coded 1500 series
390c
|  |  | EBAA Iron Sales Inc. | 1900
|  |  | Sigma | PV-Lok PWPF
1000-1100-1200G2
|  |  | SIP Industries Inc | EZ Grip PTPVC
|  |  | Ford Meter Box Co. Inc. | Uni-Flange UFR 1399
Uni-Flange 1559
Joint Restraints | For PVCO Pipe Bell and Spigot Push-On Joints | 400mm | Clow Canada | Tufgrip Dual Wedge | Orange colour coded 1500 series
390c
|  |  | Sigma | PV-Lok PWP
|  |  | Star Pipe Products Inc | 1100 Series
|  |  | SIP Industries Inc | EZ Grip PTPVC
|  |  | Ford Meter Box Co. Inc. | UFR 1559
| For PVCO Pipe to Mechanical -Joint Fitting | ASTM F1674 100mm to 300mm | Clow Canada | 300c
|  |  |  | Tuf Grip Dual Wedge | Orange colour coded 1500 series
|  |  | EBAA Iron Sales Inc. | 19MJ00
|  |  | Sigma | PWM
Sigma One-Lok SLC
|  |  |  | Stargrip 4300 Series | Orange colour coded 4300 series
PVC 4000 G2 Series
PVC 1000 G2 Series
|  |  | SIP Industries Inc | EZ Grip PTPDF
EZ Grip EZPVC
EZ Grip EZPVCNG
|  |  | Ford Meter Box Co. Inc. | Uni-Flange 1309
Uni-Flange 1500
|  | 400mm | Clow Canada | 300c
|  |  |  | Tuf Grip Dual Wedge | Orange colour coded 1500 series
|  |  | Sigma | PV-Lok PWM
One-Lok SLCE
|  |  | SIP Industries Inc | EZ Grip PTPDF
EZ Grip EZPVC
|  |  | Star Pipe Products Inc | PVC 1000 Series
PVC 4000 G2 Series
| For Ductile Iron Pipe | ASTM F1674 All complete with 304 stainless steel nuts & bolts To be installed with 3 part corrosion protection system Installed with concrete thrust blocks (on existing pipe only) in accordance with OPS standards | Star Pipe Products Inc | Stargrip 3000, Stargrip 4300
|  |  | Ford Meter Box Co. Inc. | UniFlange Series 1390D, 1400D
|  |  | Clow Canada | Tufgrip Dual Wedge | Orange colour coded 1500 series
|  |  |  | Series 400 | Flange Adapter
|  |  | SIP Industries Inc | EZ Grip for DI | Black colour coded
|  |  | Smith-Blair | 111 & 120
|  |  | Sigma Corp | One-Lok SLD
|  |  | EBAA Iron Sales Inc. | Megalug Series | 1100, 1500, 1600
|  |  | Romac Industries Inc. | Grip Ring
Connectors | For Tracer Wire | approved for direct bury | Klick-It ll -PCS Ltd | Model C8816 | Connectors shall be used on all non-metallic wms, hydrant
|  |  | Dryconn_King Innov. R | Blue (Lug Type) | laterals & non metallic water services (std dwg 1-7-10)
Couplings | Transition Couplings | Restrained Meeting AWWA C219, C227 and M11 or M9 Or SS body conforming to ASTM A240 316/316L Complete with T-304 Stainless steel nuts and bolts Centre sleeves and end rings shall be shop coated | Dresser Piping Specialities | Style 53 and 153 | Couplings must be self restrainer type or installed with AWWA C111 approved fasteners
|  |  | Straub Tadco Manufacturing | Struab Grip
|  |  | Cambridge | Model 3501
|  |  | Smith Blair Inc. | 470 Series | Pipe Lock restrained coupling for different pipe materials
|  |  | TPS-Cromer Ind Corp | Hymax 2000 or Large Dia. coupling | To be installed with split-ring restrainer/tie-rods
|  |  | Teekay (Taylor Kerr ltd) | Axilock
|  |  | Ford Meter Box Co. Inc. | FC1, FC2A | To be installed with approved restrainers
|  |  |  | RCPP-x | Restrained coupling, for pipe with same nominal OD, PVC x PVC
|  |  | Victaulic Co.of Canada Ltd. | Style 31 | Grooved, Rigid or Flexible, for DI pipe Class 53 and above
|  |  |  | Style 44 | Grooved, Flexible, for steel pipe. To replace existing Style 44's.
|  |  | Romac Industries Inc. | 501 straight transition coupling
|  |  | YNC Pipe Couplings Inc. | YNC Pipe Couplings | All stainless steel
|  | Non-Restrained Meeting AWWA C219 and C227 Or SS body conforming to ASTM A240 316/316L Complete with T-304 stainless steel nuts and bolts Centre sleeves and end rings shall be shop coated | Robar Industries | 1406
|  |  | Teekay (Taylor Kerr ltd) | Axiflex
Repair
|  |  | Smith Blair Inc. | Model 441
|  |  | Straub Tadco Manufacturing | Straub Flex
|  |  | TPS-Cromer Ind Corp | Hymax (Large Dia)
|  |  | Ford Meter Box Co. Inc. | FC1, FC2A
|  |  | Romac Industries Inc. | 501 straight transition
|  |  | TPS-Cromer Ind Corp | Hymax 2000 Flexible
|  |  | YNC Pipe Couplings Inc. | YNC Pipe Couplings
| Flanged Coupling | Meeting AWWA C219 and AWWA C207 Class D flange Complete with stainless steel nuts and bolts Minimum ASNI Class 125 flange | Smith Blair Inc. | Model 912 | Non-restrained
|  |  | Dresser Piping Specialities | Style 128 | Non-restrained, restraint can be provided, up to 600mm
|  |  | Viking Johnson | MaxiDaptor | Non-restrained
|  |  | Robar Industries | 7406 | Non-restrained
|  |  | Victaulic Co.of Canada Ltd. | Style 341 | Restrained, For DI pipe, with grade "M" gasket
|  |  | Romac Industries | FCA 501
|  |  |  | Alpha Ex Range | Restrained, for PVCO pipe (c/w Series 1500 restrainer)
|  |  | Ford Meter Box Co. Inc. | Uni-flange RFAP | for PVCO pipe
|  |  | Clow Canada | Series 90C | for PVC pipe
|  |  |  | Series 40C | for DI pipe
| Tapped Couplings | STD DWG 1-7-1 AWWA C800 | Ipex | Blue Brute Tapped Coupling | 150mm to 200mm PVC watermains in 19mm to 50mm
|  |  | West Lake Pipe | AquaConnect Tapped Couplings | service sizes, restrained
Hydrants |  | STD DWG 1-6-1 & 1-6-2 AWWA C502 FM approved ▪Two 63.5mm diameter hose nozzles at 180 degree to each other ▪Hose nozzle and operating nut threads in accordance with Province of Ontario standards ▪Base (boot) with 150mm mechanical connection end ▪Safety breakaway flanges and breakaway couplings ▪Painted to Region of Peel specified colours (red and silver) | Mueller Canada | Canada Valve Century
|  |  | Clow Canada | Sentinel | Zinc anode installed on operating rod just above drip lever (Mueller Only)
|  |  |  | Concord D67-M | If a hydrant extension is required to adjust to the length of a hydrant barrel, it shall be obtained from the manufacturer supplying the hydrant and installed as per the manufacturers instructions
|  |  | Clow-Bibby | Dry Barrel - Model 2700 | Clow split coupling for Brigadier and Concord hydrant extensions
McAvity M67B
|  |  | AVK | 2700
Valve Box |  | Slide Type 108mm, 6mm predrilled round hole with grommet for tracer wire in upper section ASTM A48M-03 CLASS 30B | Mueller Canada | A769 with guide plate
|  |  | Clow-Bibby | VB 1100 & V800 - Lid
Conqueror B.M.Inc.
Star Pipe Products
|  |  | Cedar Infrastructure Products | N3907
|  |  | DomCast | DF64
Sigma Corp
Valve Box Extension |  | Less than or equal to 1.8m total extension length 300mm and 600mm increments | Clow Canada
Mueller Canada
Sigma Corp.
|  |  | Cedar Infrastructure Products | N3907
Star Pipe Products
Valves | Gate Valve < 100mm dia. |  | Crane |  | Rising spindle Installed in above ground applications or in chamber only
| Gate Valve 100mm - 200mm dia. |  | Mueller Canada | A-2360 | T-304 stainless steel nuts and bolts, corrosion protection system
|  |  | Clow Canada | F6102
| Resilient Wedge Gate Valve | 100mm to 300mm dia. Inclusive AWWA C509 | AVK | Series 45 | T-304 stainless steel nuts and bolts, corrosion protection system
|  |  | Clow Canada | 2639/2640 | Open left (counter clockwise)
|  |  | Mueller Canada | A-2360 | Inside non-rising stem
|  | 400mm AWWA C509, Ductile Iron Body | J & S Valve | Series 6600,6800,6900 | Fusion Bonded Epoxy (FBE) Coated
|  |  | AVK | Series 25, 45
| Check Valve |  | Mueller Canada | A-2600 | T-304 stainless steel nuts and bolts,
|  |  | Val-matic | Swingflex | Fusion Bonded Epoxy Coated Valve, inside & out
|  |  | Clow Canada | Kenflex #506 | Not to be used for backflow prevention unless two inline and certified for that purpose
| Detector Check Valve | ANSI B16.1 Class 125 Bypass inlet/oulet ports to be min 25mm Suitable for continuous submerged conditions | Zurn/Wilkins | Model 310 (up to 200mm)
|  |  | Mueller Canada | Model EDCIV (250mm) | 25mm bypass in brass only for all DCV, per STD 1-3-9
|  |  | Watts/Ames | 774 DCDA (300mm) | Meter supplied/installed by Region Meter Dept
SS07F (200 & 250mm)
1000DCV (all sizes)
| Tapping Valve | AWWA C509 | Mueller Canada | T2360
|  |  |  | A2360 | 100mm diameter and larger
|  |  | AVK | Series 45 | All taps done by Region of Peel
|  |  | Clow Canada | F6114
| Pressure Regulating Valve |  | Cla-Val | Series 90 | Model to be approved on a site specific basis
|  |  | Singer | 106-PR, 206-PR | Provided with filter canisters Provided with stainless steel rings, Fusion Bonded Epoxy (FBE) coated valve, inside & out. Stainless Steel hardware.
| Flow Control Valve |  | Cla-Val |  | Model to be approved on a site specific basis
|  |  | Singer |  | Provided with filter canisters Provided with stainless steel rings, Fusion Bonded Epoxy (FBE) coated valve, inside & out. Stainless Steel hardware.
Air Valves | Air Release |  | Vent-O-Mat | RBX | Vented
|  |  | Apco | 143C, 145C, 149C Threaded
|  |  | Val-Matic | 201C, 202C, 203C Threaded | Fusion Bonded Epoxy Coated Valve, inside & out
|  |  | Crispin | UL 10.1, UL 20.1, UL 41.1
| Air/Vacuum Release |  | A.R.I | D-040P, D-040CV
|  |  | Floval Equipment Ltd | Dezurik/APCO 'ASU'
| Air Release Backflow Preventer |  | Val-Matic | Floodsafe® | (On all air valve installations) Fusion Bonded Epoxy Coated Valve, inside & out
Backflow Preventor |  |  | Watts | Series LF909, 957 and LF009
|  |  | Cla-Val | Model 3 or R.P.
|  |  | Febco | LF825Y or LF860
Sampling Station |  | STD DWG 1-7-6 |  |  | Green Eclipse style for Caledon only
Tapping Sleeves | PVC Pipe | All tapping sleeves to be supplied with stainless steel (passive 304) nuts and bolts | Robar Industries | 6606 | With full liner
|  |  | Ford Meter Box Co. Inc. | Ford "Fast" | All stainless steel
|  |  | Romac Industries | SST
|  |  | Smith-Blair Inc | 663
|  |  | Mueller Canada | H304
| DI and CI | All tapping sleeves to be supplied with stainless steel (passive 304) nuts and bolts | Robar Industries | 6606 | With full liner
|  |  | Ford Meter Box Co. Inc. | Ford "Fast" | All stainless steel
|  |  | Romac Industries | SST
|  |  | Smith-Blair Inc | 663
|  |  | Mueller Canada | H304
|  |  |  | H613 | Ductile iron only
| Asbestos Cement Pipe (rough barrel) | All tapping sleeves to be supplied with stainless steel (passive 304) nuts and bolts | Mueller Canada | H304 SS | 350mm and larger
|  |  |  | H619 | 300mm and smaller
|  |  | Robar Industries | 6606 | With full liner
|  |  | Romac Industries | SST
|  |  | Ford Meter Box Co. Inc. | Ford "Fast" | All stainless steel
|  |  | TPS-Cromer Ind Corp | Ez-Tap Plus serv/sad | All stainless steel-full seal
|  |  | Smith-Blair Inc | 663
| PVC0 C909 | AWWA C223 | JCM | 422
|  |  | Power Seal | 3480
|  |  | Smith-Blair Inc | 622
|  |  | Ford Meter Box Co. Inc. | Ford "Fast"
|  |  | Romac | FTS419
| Concrete Pressure Pipe | Tapping sleeves to be supplied by corresponding manufacturer |  |  | Spec to CPP C-301 or C-303 Installation & tap to be done by certified installer/welder
Repair Clamps |  | All repair clamps to be supplied with stainless steel (passive 304) nuts and bolts | TPS-Cromer Ind Corp | Ez-max Repair Clamp | All stainless steel-full seal
|  |  | Robar Industries |  | All stainless steel
|  |  | Mueller Canada |  | All stainless steel
|  |  | Cambridge Brass | Teck | With taper gasket
|  |  | Teekay (Taylor Kerr ltd) | Repair | All stainless steel-full seal
|  |  | Straub-Tadco Inc | Straub Clamp
|  |  | Romac Industries | LSS1 | 1 piece with full seal
|  |  | YNC. Pipe Couplings Co. |  | All stainless steel
|  |  | Clow Canada | Concord D76R - Series 200
| Bell Joint Repair Clamps | All repair clamps to be supplied with stainless steel (passive 304) nuts and bolts | Smith-Blair Inc. | 274
|  |  | Romac Industries | 516
|  |  | Dresser | 60 and 160
Main Stops (Corporation) All brass water service fittings are 'no lead' (5 ppb) as per NSF 61 Annex F | 19mm and 25mm | Compression type - Stainless Steel Ball style same size inlet and pack joint Saddles to be used on all PVC pipe Torque shall be between 37 Joules and 47 Joules (27 ft-lb to 35 ft-lb) | Ford Meter Box Co. Inc. | FB1000-X- NL
|  |  | Cambridge Brass | Series 301NL
|  |  | Mueller Canada | Series 300N
|  |  | A.Y. McDonald Mfg. | 74701BQ | Do not use serrated jaw wrenches to tighten any main stop.
|  |  |  | 74701BT | Teflon tape to be added to all listed main stops.
| 40mm and 50mm | Compression type - Stainless Steel Ball style same size inlet and pack joint Saddles to be used on all PVC pipe Torque shall be between 37 Joules and 47 Joules (27 ft-lb to 35 ft-lb) | Cambridge Brass | Series 301NL | Tighten to stop feature with copper continuity.
|  |  | A.Y. McDonald Mfg. | 76100T | No copper continuity.
|  |  |  | 76100Q | Do not use serrated jaw wrenches to tighten any main stop.
|  |  | Ford Meter Box Co. Inc. | FB1000-X- NL
|  |  | Mueller Canada | Series 300N
| 40mm and 50mm | for non metallic pipe use main stop with tracer wire hole | Cambridge Brass | 301-A-HE(NL)
|  |  | Ford Meter Box Co. Inc. | Ballcorp FB1000-X-TW-Q (NL)
Water Service (19mm - 50mm) | Copper | Type K Soft Copper ASTM B88-49 STD DWG 1-7-1 |  |  | Zinc Anode installed 1m minimum form curb stop as per OPSS 442 & OPSD 1109.010
| Polyethylene | AWWA C901 CSA B.137 STD DWG 1-7-1 |  |  | Due to outside diameter, sizing of pipe shall be one size larger, i.e. 25mm nominal size where 19mm is specified Stainless steel inserts required, in accordance with manufacturers recommendations 12 gauge TWU stranded copper, light coloured, plastic coated tracer wire to be installed with all non-metallic pipe. Main stops, curb stops and service boxes must be designed to specifically accommodate TWU. (see Type for detailed infromation)
Service Saddles (must be double bolt, for all service taps) | PVC Class 150 |  | Clow | D72
|  |  | Romac | 306 double bolt
|  |  | Robar | 2706 double strap
2616
|  |  | Smith Blair | 370 Series
|  |  | Cambridge | 403 Broad Band
3412AS
3416AS
|  |  | Ford Meter Box Co. Inc | FS313 | Single band
|  |  |  | FS323 | Double band
|  |  | Continental Ind. | PVC Fast Tap
|  |  | Clow | D72
|  |  | Mueller | H13428
H13431
H13433
|  |  | Robar | 2616
|  |  | Cambridge | 403 Broad Band
| PVC Class 160, Series 100 |  |  | 3412AS
3416AS
|  |  | Romac | 306 double bolt
|  |  | Concord Daigle | D71
|  |  | Smith Blair | 370 Series
Service Saddles (must be double bolt, for all service taps) |  |  | Ford Meter Box Co. Inc | FS313 | Single band
|  |  |  | FS323 | Double band
|  |  | Continental Ind. | PVC Fast Tap
| C.I. and D.I. |  | Clow | D72
|  |  | Robar | 0406 | With s.s bales
|  |  | Smith Blair | 313 | Ductile Iron Double Bale Service Saddle
|  |  | Ford Meter Box Co. Inc | FS313 | Single Band
|  |  |  | FS323 | Double Band
|  |  | Romac | 306 double bolt
|  |  | Cambridge | 403 Broad Band (Teck)
3412AS
3416AS
| PVCO C909 | AWWA C800 | Canada Pipeline Accs | SC-2 Double Bolt
|  |  | Cambridge Brass | 8403 Double Bolt
|  |  | Robar | 2616 Double Bolt | 2406/2506 (Cast DI)
|  |  | Ford Meter Box | FS313 Double Bolt
| Asbestos |  | Smith Blair | 323 | Ductile Iron Double Bale Service Saddle
|  |  | Romac | 306 double bolt
|  |  | Cambridge | 403 Broad Band(Teck)
3412AS
3416AS
| Concrete | Manufactured to suit AWWA C301, C303 pipe accordingly Welded outlets are to be as per pipe manufacturer recommendations | Smith Blair | 362 | T-304 stainless steel nuts and bolts
Curb Stops | 19mm to 50mm Must be 'no lead' (5 ppb) as per NSF 61 Annex F | Compression type - Stainless steel Ball style | Ford Meter Box Co. Inc. | B44 Series NL
Z44 Series NL
BH 44-233G NL
4713T NL
|  |  | Mueller Canada | H 15207N
H15209N
|  |  | A.Y. McDonald | 76100T
76100Q
|  |  | Cambridge Brass | 202NL
| 19mm to 50mm Must be 'no lead' (5 ppb) as per NSF 61 Annex F | for non metallic pipe use Curb Stop with tracer wire insert | Cambridge Brass | 202-H-HE NLseries | Non metallic pipe must be installed with tracer wire compatible appurtenances
|  |  | Ford Meter Box Co. Inc. | B44-XXX-TW-Q-NL
Service Box |  | To be supplied with stainless steel rod and brass cotter pin For 1.52m to 1.83m bury, use rod 1.14m long. Extension required if special depths are encountered (as per manufacturers recommendations). | Mueller Canada | A726 | 19mm - 25mm
|  |  |  | A728 | 40mm - 50mm
|  |  | PCHG | D2N | 40mm - 50mm
|  |  |  | D1N | 19mm - 25mm
|  |  | Clow Canada | D1 | 19mm - 25mm
|  |  |  | D2 | 40mm - 50mm
|  |  | Bibby | VSB1 | 19mm - 25mm
|  |  |  | VSB2 | 40mm - 50mm
Conqueror BMI
|  |  | Cedar Infrastructure Products | N3909 | 19mm - 25mm
|  |  | Sigma Corp. | #8
|  |  | Star Pipe Products | SB-5001 | 19mm - 25mm
|  |  |  | SB-5002 | 40mm - 50mm
|  | for non metallic pipe use service box with tracer wire hole | Ford Meter Box Co. Inc. | Curb Box EM2-XX-5X-TW | Non metallic pipe must be installed with tracer wire compatible appurtenances
Casing Spacers |  | T-304 Stainless Steel | Cascade | CCS-1320-8 | Ultra high molecular weight polymer runners (or equivalent)
|  |  | Cambridge | Model 4810 | Position of pipe within liner to be centered and restrained, sufficient to provide no less than 19mm clearance between casing and bell of pipe
|  |  | Advanced Product Systems | SSI | Stainless steel bands & glass filled polymer runners
|  |  | CCI Pipeline Systems | CCS8 and CCS12 | Watermain restrained laterally for the entire length of the liner
|  |  | BWM |  | Sealed using wrap around rubber ends complete with stainless steel (T-304) banding
Precast Chamber and components | Concrete | STD DWG 1-1-5, 1-1-6, 1-1-7 CSA A257.4 OPSS 1351 | Con Cast Pipe
Omni Precast
Rinker Materials
Decast Concrete Products
Chamber Frame and Cover | Standard | OPSD 401.01 - Type A, no lugs STD 2-5-13 | Bibby Ste. Croix |  | Cast Iron, square frame with circular closed or open cover
Delta
EJ
Mueller
Cedar Infrastructure Products
Sigma Corp.
| Water Tight | OPSD 401.03, no lugs | Mueller |  | Frame to be attached to the precast section as per STD DWG 2-2-3a or 2-2-3b
Bibby Ste. Croix
Cedar Infrastructure Products
EJ
Chamber Adjusment Units | Pre-Cast Concrete | OPSS 1853 | Decast
|  |  | Rinker Materials | Moduloc
| Polyethylene | OPSS 1853 | Ipex | Lifesaver
Anodes | High Potential Magnesium | ASTM B843 OPSS 442 | Interprovincial Corrosion Control Co Ltd. | 32D5GG | 3m AWG#10/7 strand copper wire c/w RWU-90 insulation
|  |  | Bren Tech |  | Size of anode as per design
|  |  | Maple Agencies | Exothermal Ind.MA-32
| High Purity Zinc | ASTM B418 OPSD 1109.011 | Bren Tech | 5.5kg for 25mm copper services every | As per STD DWG 1-7-1, installed with brass ground clamp,
|  |  | Maple Agencies | 20m and for 50mm copper services every | (as per OPSS 422 Table 1 and 4)
|  |  | Intergity Anode Corporation | 16m
*The approved products list pertains to water appurtenances equal to or less than 400mm